INSPECTION & TEST PLAN

REINFORCED CEMENT CONCRETE WORKS

QA-XXX-YYY-ITP-STR-RCC-R3

| 0 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Revision | Date | Written by | Checked by | Approved by | Remarks |

| Revision | Revision History |
| --- | --- |
| 0 | First issue |

|  |  |  | Project | (PROJECT NAME) |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| INSPECTION & TEST PLAN REINFORCED CEMENT CONCRETE WORKS |  |  |  |  |  |  |  |
| Prepared by |  | Date |  | ITP No. | QA-XXX-YYY-ITP-STR-RCC | Rev. No. | 0 |
| LEGEND: CON CONTRACTOR / IP = INSPECTION PARTY / CL = CLIENT R = REVIEW / S = SURVEILLANCE W=WITNESS / H=HOLD POINT |  |  |  |  |  |  |  |  |

| # | Submission / Inspection / Test details | Method | Inspection |  |  | Frequency | QC Approval By | Acceptance Criteria | Verification Record (register, inspection, test) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | CON | IP | CL |  |  |  |  |
| 1 | DOCUMENTATION REVIEW |  |  |  |  |  |  |  |  |
| 1a | Shop drawings & Detailed Section & Elevation Drawings | Review | H | H |  | 2-4 Weeks Prior to commencing of works | PM/ CM | In accordance to contract specs, Design requirement, drawings | Contractor’s documentation |
| 1b | Steel manufacturer details | Review | H | H |  |  | PM/CM/ QE | Approved supplier and product as per contract specs |  |
| 1c | RMC supplier & batching plant details | Review | H | H |  |  | PM/CM/ QE | As per contract specs and details, ACT QC guidelines & schedule Valid calibration certificates |  |
| 1d | Concrete mix design | Review | H | H |  |  | PM/CM/ QE | As per contract specs and details, (if Contractor’s batching plant is used, refer to specific batching plant ITP) |  |
| 1e | Bar bending schedule, Method statement | Review | H | H |  |  | PM/CM/ QE | As per contract specs and standards |  |
| 1f | Formwork Detailed design and method of erection details | Review | H | H |  |  | PM/CM/ QE | As per contract specs and drawings and standards |  |
| 1g | Trial mix approval | Visual/Review of results | H | H |  |  | PM/CM/ QE | As per contract specs and Standards | Lab Test Results |
| 2 | INSPECTION OF INCOMING MATERIALS: |  |  |  |  |  |  |  |  |
| 2a | CEMENT | Refer to ITP for Civil Work Materials and Batching plant ( QA-ACT-PM-CWM-R2 ) |  |  |  |  |  |  |  |
| 2b | REINFORCEMENT BARS |  |  |  |  |  |  |  |  |
| 2c | AGGREGATES & ADMIXTURES |  |  |  |  |  |  |  |  |

| # | Submission / Inspection / Test details | Method | Inspection |  |  |  |  | Frequency |  | QC Approval By | Acceptance Criteria |  | Verification Record (register, inspection, test) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | CON |  | IP |  | CL |  |  |  |  |  |  |
| 2d | READY MIX CONCRETE | Refer to ITP for Civil Work Materials and Batching plant ( QA-ACT-PM-CWM-R2 ) |  |  |  |  |  |  |  |  |  |  |  |
| 3 | FORM- WORKS INSPECTION |  |  |  |  |  |  |  |  |  |  |  |  |
| 3a | Check for access/ platform | Visual |  |  |  |  |  | All | QE |  |  | Proper access and suitable platform for verticals to be provided | Inspn: record CHECKLIST |
| 3b | Check for location, position, dimensions and shape | Visual |  |  |  |  |  | All | QE |  |  | As per approved drawings and details |  |
| 3c | Check for props, studs, wedges | Visual / Mmnt |  |  |  |  |  | All | QE |  |  | As per approved drawings and details |  |
| 3d | Check for Level of casting | Visual / Mmnt |  |  |  |  |  | All | QE |  |  | Casting level to be marked as per approved drawings and details |  |
| 3e | Check for verticality w.r.t lower floors | Visual / Mmnt |  |  |  |  |  | All | QE |  |  | Within the specified tolerence |  |
| 3f | Check for tolerance on plumb, alignment | Visual / Mmnt |  |  |  |  |  | All | QE |  |  | Dimensions of cross-section of columns and beams -- +6mm/-12mm |  |
| 3g | Form release agent | Visual |  |  |  |  |  | All | QE |  |  | Suitable material pre approved to be applied |  |
| 3h | Check for water tightness | Visual / Mmnt |  |  |  |  |  | All | QE |  |  | All gaps and holes to be sealed with suitable means to make any leakage of slurry |  |
| 4 | REBARS WORKS INSPECTION |  |  |  |  |  |  |  |  |  |  |  |  |
| 4a | Bending, cutting | Visual |  |  |  |  |  | All | QE |  |  | As per approved BBS(bar bending schedule) | Inspn: record CHECKLIST |
| 4b | Check for cleanness of rebars | Visual |  |  |  |  |  | All | QE |  |  | All rebars to be clean from mill scale, cement, grout etc |  |
| 4c | Fixing/Placing Size , Spacing, No of bars, Anchorage & Laps | Visual |  |  |  |  |  | All | QE |  |  | As per approved structural drawings. |  |
| 4d | Check for inserts | Visual / Mmnt |  |  |  |  |  | All | QE |  |  | As per approved drawings / details |  |
| 4e | Binding wire | Visual / Mmnt |  |  |  |  |  | All | QE |  |  | ≥ 0.90mm thick. Wire knots’ are not in cover zone. Free ends to be bend inwards |  |
| 4f | Cover Blocks | Visual / Mmnt |  |  |  |  |  | All | QE |  |  | ≤ 600mm, As per RCC drawing. Same as concrete. Precast & cured. |  |
| 4g | Chairs - | Visual / Mmnt |  |  |  |  |  | All | QE |  |  | ≤ 1.0 m, spanning across min 3 bars. Or as per appd. details |  |
| 4h | All hooks (stirrups, loops, ties) | Visual / Mmnt |  |  |  |  |  | All | QE |  |  | Bent at 135 degree. |  |

| # | Submission / Inspection / Test details | Method | Inspection |  |  | Frequency |  | QC Approval By | Acceptance Criteria | Verification Record (register, inspection, test) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | CON | IP | CL |  |  |  |  |  |
| 5 | CONCRETE WORKS |  |  |  |  |  |  |  |  |  |
| 5a | Cleaning | Visual / Mmnt |  |  |  | All | QE |  | All binding wire pieces and unwanted materials to be removed and to be properly cleaned using suitable means | Inspn: record CHECKLIST |
| 5b | Check for MEP clearance | Visual |  |  |  | All | QE |  | All MEP works to be completed and MEP approval to be obtained prior to start |  |
| 5c | Check stoppers | Visual |  |  |  | All | QE |  | As per approved structural drawings. |  |
| 5d | Check inserts | Visual |  |  |  | All | QE |  | As per approved structural drawings. |  |
| 5e | Placing concrete | Visual |  |  |  | All | QE |  | To be start within 30 min Max: freefall is 1m To be done in layers without segregation No displacement to rebars |  |
| 5f | Vibrating concrete | Visual |  |  |  | All | QE |  | Sufficient no: of vibrators with stand by Avoid segregation and bleeding |  |
| 5g | Tamping , leveling / surface finish | Visual |  |  |  | All | QE |  | As per spec: requirements |  |
| 5h | Check for construction/ Control joints | Visual |  |  |  | All | QE |  | As per approved structural drawings. |  |
| 5i | Casting Cubes | Visual / Mmnt |  |  |  |  |  |  |  |  |

| # | Submission / Inspection / Test details | Method | Inspection |  |  | Frequency |  | QC Approval By | Acceptance Criteria | Verification Record (register, inspection, test) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | CON | IP | CL |  |  |  |  |  |
| 6 | POST CONCRETE WORKS INSPECTION. |  |  |  |  |  |  |  |  |  |
| 6a | Check for surface cracks | Visual |  |  |  | All | QE |  | All surface cracks to be closed before final setting | Inspn: record CHECKLIST |
| 6b | Curing | Visual |  |  |  | All | QE |  | Surface wet at all times for 14 days/ or as specified |  |
| 6c | Check levels | Visual / Mmnt |  |  |  | All | QE |  | ± 5mm |  |
| 6d | Check Cement Consumption. | Visual/ Mmnt |  |  |  | All | QE |  | As per mix design. |  |
| 6e | Check for stripping | Visual |  |  |  | All | QE |  |  |  |
| 7 | NCR and Inspection after Rectification of Defects | Refer to NCR Procedure in case of non-compliance of tender/contract conditions. |  |  |  |  |  |  |  | Non-Conformance Report |  |  |

|  |  |  |  | Project | Project Name |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| INSPECTION RECORD REINFORCED CEMENT CONCRETE WORKS |  |  |  |  |  |  |  |
| ITP | RCC WORKS | Inspection No. | QA-XXX-YYY-ITP-STR-RCC-_________ |  |  | Location |  |
| Prepared by |  |  | Applicable Drawing |  |  |  |  |

| # | Description |  | Result |  | Date | Sign |  | # |  | Description | Result |  | Date | Sign |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | Cont: | IP |  |  |  |  |  |  | Cont: | IP |
| 3 | FORM- WORKS INSPECTION |  |  |  |  |  |  | 4h |  | All hooks (stirrups, loops, ties) |  |  |  |  |  |
| 3a | Check for access/ platform |  |  |  |  |  |  | 5 |  | CONCRETE WORKS INSPECTION |  |  |  |  |  |
| 3b | Check for location, position, dimensions and shape |  |  |  |  |  |  | 5a |  | Cleaning |  |  |  |  |  |
| 3c | Check for props, studs, wedges |  |  |  |  |  |  | 5b |  | Check for MEP clearance |  |  |  |  |  |
| 3d | Check for Level of casting |  |  |  |  |  |  | 5c |  | Check stoppers |  |  |  |  |  |
| 3e | Check for verticality w.r.t lower floors |  |  |  |  |  |  | 5d |  | Check inserts |  |  |  |  |  |
| 3f | Check for tolerance on plumb, alignment |  |  |  |  |  |  | 5e |  | Placing concrete |  |  |  |  |  |
| 3g | Form release agent |  |  |  |  |  |  | 5f |  | Vibrating concrete |  |  |  |  |  |
| 3h | Check for water tightness |  |  |  |  |  |  | 5g |  | Tamping , leveling / surface finish |  |  |  |  |  |
| 4 | REBARS WORKS INSPECTION |  |  |  |  |  |  | 5h |  | Construction/ Control joints |  |  |  |  |  |
| 4a | Bending, cutting |  |  |  |  |  |  | 5i |  | Casting Cubes |  |  |  |  |  |
| 4b | Check for cleanness of rebars |  |  |  |  |  |  | 6 |  | POST CONCRETE WORKS INSPECTION. |  |  |  |  |  |
| 4c | Fixing/Placing Size , Spacing, No of bars, Anchorage & Laps |  |  |  |  |  |  | 6a |  | Check for surface cracks |  |  |  |  |  |
| 4d | Check for inserts |  |  |  |  |  |  | 6b |  | Curing |  |  |  |  |  |
| 4e | Binding wire |  |  |  |  |  |  | 6c |  | Check levels |  |  |  |  |  |
| 4f | Cover Blocks |  |  |  |  |  |  | 6d |  | Check Cement Consumption. |  |  |  |  |  |
| 4g | Chairs - |  |  |  |  |  |  | 6e |  | Check for stripping |  |  |  |  |  |
| CONCLUSION |  | Accepted Accepted with Comments Rejected NCR No. _______ |  |  |  |  |  |  |  |  |  |  |  |  |  |
| COMMENTS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| CONTRACTOR |  |  |  |  |  |  |  |  | INSPECTION PARTY |  |  |  |  |  |  |
| Sign |  |  |  | Date |  |  |  |  | Sign |  |  | Date |  |  |  |

|  |  | Project |  | PROJECT NAME |  |
| --- | --- | --- | --- | --- | --- |
| REQUEST FOR DE-SHUTTERING OF SLABS |  |  |  |  |  |
| Contractor |  |  | Request date |  |  |

DESCRIPTION:  ……………………………………………………………………………………………………….

…………………………………………………………………………………………………………………….

…………………………………………………………………………………………………………………….

Slab Casted on ____ / ___ / ____

De shuttering and back propping to be done

Slab casted on ____ / ___ / ____

Slab casted on ____ / ___ / ____

| CONCLUSION |  | Accepted Accepted with Comments Rejected NCR No. ____________ |  |  |
| --- | --- | --- | --- | --- |
| COMMENTS |  |  |  |  |
|  | CONTRACTOR |  | INSP: PARTY (QA/QC) | INSP: PARTY (SAFETY) |
| Name |  |  |  |  |
| Sign |  |  |  |  |
| Date |  |  |  |  |